Literature Review of the Model based open-loop correction of heliostat tracking errors

The Heliostat field is by far the most expensive part of a typical Central Receiver(CR) palnt. To achieve high conversion effiencies, heliostats with very high tracking accuracy are needed, but errors are introduced due to manufacturing, installation, and alignment tolerances as well control system granularity. Mechanical error profiles are unique for every heliostat and cause tracking errors that vary over the course of days and seasons and therefore cannot be corrected by once-off angle offset corrections. Developments in microcontroller technology drives decentralisation of CR control systems . Powerful open-loop error correction algorithms can run on low cost heliostat local controllers, enabling high tracking accuracy from lower cost heliostats with reduced tolerances.

This paper describes the development of a scalable, modular and adaptable control system aimed at low cost heliostats deployed on rough, non-flat terrain without the need for accurate surveying of installed locations or precision structure leveling before installation. This involved (Baheti and Scott) developing a model based heliostat error mechanism method to compensate for mechanical errors inherent in typical heliostat mechanisms. This model included a pedestal tilt, azimuth and elevation bias offsets, drive wheel radius errors and non-orthogonal drive axes. A closed loop sensor was used to periodically point the heliostat normal vector directly at the sun. Heliostat pointing errors were obtained by comparing the commanded heliostat position at each interval with the actual solar position as calculated by solar algorithm. The data was used to calculate to estimate coefficients for error model and resulted in final RMS error reductions of 10:1 and 5:1 for azimuth and elevation tracking respectively. This and other model-based methods were initially now widely implemented due to the high cost and practical constraints of computers at the time.
Kenneth Stone added the effects of non-orthogonal drive axes to (Baheti and Scott model)

The development of a modular heliostat control architecture using a model based tracking error correction method was described and validated experimentally. The heliostat is being expanded to incorporate linear actuator driven fixed horizontal and azimuth elevation heliostats with slew driven azimuth axis and linear actuator driven elevation axis.

Literature Review for Solar Tracking Fuzzy Control System Design using FGPA
A solar tracking generating power system is designed and implemented. A controller, sensors and I/O interface are integrated with a tracking mechanism to increase the energy generation of solar cells. In order to track the sun, cadmium sulfied light sensitive resistors are used. To achieve optimal solar tracking, a fuzzy algorithm is developed. A field programmable gate array is applied to design the controller such that the solar cells always face the sun in most of the day time. The tracking light sensor can deliver different signals to the FGPA controller through an analog/digital converter according to different sunlight intensity. When the voltage on eastward-westward direction or the southward-northward direction is different, the differences will be delivered into a fuzzy controller which produces pulses to motor drives that produces PWM signal to control step motor for tuning desired angles
The array solar tracking system architecture contains two motors to drive the platform, conducting an approximate hemispheroidal three-dimensional rotation on the array solar
generating power system
The tracking device is composed of four same CdS (Cadmium Sulfide) light sensitive resistors, which detect light intensity from eastern, we
stern, southern, and northern directions, respectively. In every direction, there is a CdS light sensitive resistor with an elevating angle 45oto face a light source. The four sensors are separated as two groups.
One is using two CdS light sensitive resistors to be an eastward-westward direction sensor for comparing the light intensity of eastward and westward directions. When the eastward-westward direction sensor receives different light
intensity, the system will obtain the signal according to the output voltages of the eastward-westward direction sensors.

Solar Zenith Angle
Solar Zenith Angle is the angle between the zenith and the center of the Sun’s disc.
Zenith is the imaginary point directly above a particular location, on the imaginary celestial sphere.
The solar elevation angle is the altitude of the Sun, the angle between the horizon and the center of the Sun’s disc. Since these angles are complementary, the cosine of either one of them equals the sine of the other. They can be calculated using results from spherical trigonometry.
(https://en.wikipedia.org/wiki/Solar_zenith_angle)

Solar altitude is the angle of the sun relative to the earth’s horizon

Hour angle is the angle between an observer’s meridian(a great circle passing over a person’s head and through the celestial poles)

Hour angle is one of the coordinates used in the equatorial coordinate system to give the direction of a point on the celestial sphere. The solar angle is an expression of time, expressed in angular measurement, usually degrees, from the solar noon. (12 pm) At solar noon, the hour angle is 0.000 degree, with the time before the solar noon expressed as negative degrees.
(https://en.wikipedia.org/wiki/Hour_angle)

It is the angle, taken to be positive to the west, measured along the celestial equator between an observer’s meridian and the hour circle
Sunset and Sunrise occur when the zenith angle is 90

Ephemeris gives the positions of naturally occuring astronomical objects as well as artificial satellites in the sky at given time
(https://en.wikipedia.org/wiki/Ephemeris)

(https://hal-mines-paristech.archives-ouvertes.fr/hal-00725987/document)
The SG2 Algorithm for a Fast and Accurate computation of the position of the sun for mulit-decadal time period

The Earth intercepts approximately 180 * 10^6 GW of the power emitted by the Sun. The amount of power received at a given geographical site at the Earth surface varies with time: between day-night due to the Earth’s rotation and between seasons because of the Earth’s orbit and Earth’s axis inclination. At a given it also varies in space, because of the changes in the obliquity of the solar rays with longitude and latitude. Accordingly, the amount of power received at a given location, plan orientation and time depends on the relative position of the Sun and Earth. This is why both Sun-Earth geometry and time play an important role in solar energy conversion and photo-energy systems. Technological advances and increasing deployment of such systems result in an increasing demand for more accurate knowledge on the position of the Sun with respect to a system.

Reda, Andreas (2003, 2004) propose the solar position algorithm, called SPA, for solar radiation applications. It is based on the VSOP87 solutions to planetary theories (Bretagnon and Francou, 1988) and the equations by Meeus(1999). The uncertainty in terms of standard deviation of solar azimuth and elevation angles is stated to be within 5 microrad for a very large period from -2000 to 6000.The number of operations required for one computation of the solar position is approximately 1000 additions, 1300 multiplications and 300 callas of direct or inverse trigonometric functions. The algorithm is not fast enough for the purpose: an implementation in C of SPA on a 8- CPU machine would take approximately 2h for the computation of the sun.

Review of the Precise Sun-Tracking Control of Heliostats based on a Sun’s image reference system
The paper discussed existing deficiencies and problems of existing solar power generation such as the high investment cost in power plant, the energy collecting device heliostat costs more than 50% of the total cost and difficulty in realizing high precise concentrated control of heliostats.
The heliostat sun-tracking control in built solar tower power stations are mostly accomplished by means of open-loop sun-tracking based on a standalone program control or program control coupled with sun-sensor control method [5][6][7]. These methods produced accumulative errors, automatic reset and low-precision.

The motion trajectory information of a single heliostat is sampled by using a sun’s image reference system combined with machine vision based method. Nonlinear optimization was proposed to get the best image of the sun fitted to achieve a set of heliostat model parameters automatic intelligent calibration, which overcome the sun-tracking and concentrating precision drift caused by mechanical wears of the heliostat, environmental and seasonal variations to achieve high focusing rate and efficiency of energy collected. The effectiveness of proposed modelling, calibration and control theory of heliostats were verified through theoretical simulation and experimental researches.

The Sun’s image reference system (Beam Characterization System)
The heliostat parameters used for system calibration includes a machine-version system with camera[connected to a computer control system] (C) directed toward the BCS board to capture the image reflections of the sun from the heliostat. A method of online estimating heliostat parameters for open-loop sun-tracking is employed using a nonlinear [using expressions that include relationships in which variables are taken to powers other than one] optimization method to realize the minimization error calculation

Fig 1. Heliostat calibration system with BCS and machine-version

The geometry of the reflections from a heliostat surface is illustrated in Fig. 1 with the unit vectors S and R. Vector S represents the direction from the center point of the mirror of a heliostat to the Sun which is obtained by the Sun position. Vector R represents the direction from the center point of the mirror of heliostat (xo,yo,zo) to the aim point on the receiver (xR,yR,zR). The computer control system gives commands to rotate the axis A and B to change the altitude angle θ1 and azimuth angle θ2 to change the orientation of the mirror surface. The normal vector of the mirror surface NR bisects the angle between S and R to reflect sunlight to the aim receiver, and the heliostat is said to be tracking or on sun.

Fig2. Photo of Sun’s image reference system

Simulation Experiments were conducted using geographic information data in Hangzhou City, China to verify the effectiveness of the model proposed in a 1m * 1m square mirrored heliostat and a 4m * 4m square metal board BCS system. The Sun tracking reflected image center is illustrated by “▲” and the center of the BCS board “●”as the aim point.

MERITS
1. The heliostats can reach high efficiency solar collecting with no closed loop sensors.
2. Reduction of heliostat investment cost.

DEMERITS
Liable to cosine losses, astigmatism and shadowing when used for heliostat fields.

REFERENCES
[5] California Energy Commission, Solar two central receiver, http://www.energy.ca.gov/reports/2002-01-10_600-00-017.PDF,
[6] Y.T. Chen, A. Kribus, B.H. Lim, J. Karni, R. Buck, T. P. Bligh et al, Comparison of two sun tracking methods in the application of a heliostat field Journal of Solar Energy Engineering, Vol. 126. No.2, 638-644, 2004
[7] K.K. Chong, C.W. Wong, F.L. Siaw, T.K. Yew, S.S. Ng, M.S. Liang et al, Integration of an on-axis general sun-tracking formula in the algorithm of an open-loop sun-tracking system, Sensors, Vol. 9, No. 10, 7849-7865, 2009